## Sheet1
AGM Standby Use Battery > NM Series
NM12-120
12V120Ah / 10hr rate
Introduction | [7 empty] | Battery Picture & Terminal Layout
Genergy NM (33Ah-250Ah) series is designed for standby use with 10-year design life in float service. The series battery is featured of high consistency, excellent performance and reliable standby service life. It is widely applied in float service, UPS/EPS, medical equipment, telecom, photovoltaic, control system and security system.
Battery Features
○ Absorbent Glass Mat (AGM) Technology for efficient gas recombination of up to 99% maintenance free and fixed orifice plate pasting technology ○ Low self-discharge ○ Fully tank formed plates ○ Low impurity electrolyte ○ Flame retardant ABS casing with UL94-V0 is available upon request. ○ Very high purity lead
Terminal Type: T13
Electrical Specification
Design floating Life @ 25°C (77°F) |  |  |  | …………………… |  | 10 years
Nominal Capacity @ 25°C /77°F
20 hour rate |  | 6.24A to 1.75Vpc |  | …………………… |  | 124.8 Ah
10 hour rate |  | 12.17A to 1.75Vpc |  | …………………… |  | 121.7Ah
Internal Resistance
(Fully charged battery @ 25°C /77°F ) …………. | [5 empty] | 5mΩ |  | Dimension & Weight
Max. Discharge Current @ 25°C /77°F ………….. | [5 empty] | 1200 A (5S) |  | Dimension (± 2mm) | [7 empty] | Weight (± 2%)
Charge Methods: Constant voltage charge @ 25°C /77°F | [7 empty] | Length |  | Width |  | Height |  | Total Height
Cycle Use ……………………………………… | [5 empty] | 14.7 ~ 14.9V |  | 407 | mm | 173 | mm | 233 | mm | 233 | mm | 34.6 | kg
Max. Current ………………………………….. | [5 empty] | 35 A |  | 16.0236 | inch | 6.811 | inch | 9.1732 | inch | 9.1732 | inch | 76.2799 | lbs
Standby Use ………………………………….. | [5 empty] | 13.6 - 13.8V
Operating Temperature Range …………………… | [5 empty] | -30 ~ 50°C |  | Typical Applications
Notes: battery voltage must be adjusted according to temperature. | [7 empty] | ○ Telecommunications |  |  | ○ Power Utility |  | ○ Data Center |  | ○ UPS & EPS
Please refer to our recommendation.
Self-Discharge | [7 empty] | Certificates
3% of capacity declined per month @ 25°C (77°F).
Constant Current Discharge (Amperes @ 25°C /77°F)
V/cell | 10min | 15min | 20min | 25min | 30min | 35min | 40min | 45min | 50min | 55min | 1hr | 2hr | 3hr | 4hr | 5hr | 10hr | 20hr
1.6 | 287.6113 | 219.5506 | 189.6656 | 159.7806 | 135.241 | 125.6394 | 117.159 | 109.4032 | 102.2949 | 96.1391 | 90.8576 | 49.2582 | 35.0492 | 28.5437 | 23.3376 | 12.4697 | 6.2979
1.65 | 273.1099 | 208.4808 | 181.0774 | 153.674 | 131.616 | 122.3149 | 114.2527 | 106.8986 | 100.2114 | 94.4767 | 89.6237 | 48.3056 | 34.378 | 27.9453 | 22.7991 | 12.4097 | 6.2979
1.7 | 261.831 | 199.871 | 173.9278 | 147.9846 | 127.3868 | 118.2649 | 110.5195 | 103.4593 | 97.091 | 91.6751 | 87.156 | 46.6751 | 33.5846 | 27.2871 | 22.2605 | 12.2898 | 6.2979
1.75 | 249.7465 | 190.6462 | 166.1668 | 141.6875 | 122.5535 | 113.7979 | 106.5759 | 100.0164 | 94.175 | 89.2861 | 85.3053 | 45.3836 | 32.8523 | 26.6887 | 21.7818 | 12.1699 | 6.2391
1.8 | 236.8564 | 180.8064 | 157.9959 | 135.1853 | 117.7202 | 109.2281 | 102.4268 | 96.2631 | 90.8453 | 86.3798 | 82.8376 | 43.7531 | 32.059 | 26.0304 | 21.2432 | 11.8527 | 6.1802
Constant Power Discharge (Watts/cell @ 25°C /77°F)
V/cell | 10min | 15min | 20min | 25min | 30min | 35min | 40min | 45min | 50min | 55min | 1hr | 2hr | 3hr | 4hr | 5hr | 10hr | 20hr
1.6 | 499.493 | 381.2924 | 335.5559 | 289.8194 | 252.6355 | 235.2966 | 218.5727 | 203.1945 | 188.899 | 176.8258 | 165.6468 | 91.0581 | 66.2643 | 53.9159 | 44.4013 | 24.8794 | 13.1256
1.65 | 481.769 | 367.7626 | 324.3208 | 280.879 | 245.9897 | 229.0645 | 212.9705 | 198.1889 | 184.5275 | 173.0884 | 162.5622 | 89.2107 | 65.6541 | 53.3175 | 43.8029 | 24.6396 | 13.1256
1.7 | 463.2395 | 353.6179 | 312.2729 | 270.928 | 238.1355 | 221.7928 | 206.5365 | 192.5554 | 179.7373 | 169.1416 | 159.4776 | 87.0581 | 64.4336 | 52.39 | 43.1447 | 24.16 | 12.949
1.75 | 443.0986 | 338.2432 | 299.2037 | 260.1642 | 229.6772 | 213.8984 | 199.4811 | 186.2976 | 174.324 | 164.5729 | 155.7761 | 84.292 | 62.6028 | 51.1034 | 42.3668 | 23.9801 | 12.7136
1.8 | 421.3465 | 321.6386 | 285.1131 | 248.5876 | 220.6147 | 205.3814 | 191.8043 | 179.4154 | 168.2876 | 159.3823 | 151.4577 | 81.3089 | 60.9552 | 49.8169 | 41.4093 | 23.7403 | 12.5958
Subject to revision without notice. Please contact our sales representatives for latest version. | [15 empty] | Page 1 of 2
Web:www.genergybattery.com 丨 Email:sales@genergybattery.com
AGM Standby Use Battery > NM Series
NM12-120
12V120Ah / 10hr rate
Graphs
Subject to revision without notice. Please contact our sales representatives for latest version. | [15 empty] | Page 2 of 2
Web:www.genergybattery.com 丨 Email:sales@genergybattery.com