## Sheet1
AGM Standby Use Battery > NM Series
NM12-135
12V135Ah / 10hr rate
Introduction | [7 empty] | Battery Picture & Terminal Layout
Genergy NM (33Ah-250Ah) series is designed for standby use with 10-year design life in float service. The series battery is featured of high consistency, excellent performance and reliable standby service life. It is widely applied in float service, UPS/EPS, medical equipment, telecom, photovoltaic, control system and security system.
Battery Features
○ Absorbent Glass Mat (AGM) Technology for efficient gas recombination of up to 99% maintenance free and fixed orifice plate pasting technology ○ Low self-discharge ○ Fully tank formed plates ○ Low impurity electrolyte ○ Flame retardant ABS casing with UL94-V0 is available upon request. ○ Very high purity lead
Terminal Type: T13
Electrical Specification
Design floating Life @ 25°C (77°F) |  |  |  | …………………… |  | 10 years
Nominal Capacity @ 25°C /77°F
20 hour rate |  | 7.16A to 1.75Vpc |  | …………………… |  | 143.2 Ah
10 hour rate |  | 13.96A to 1.75Vpc |  | …………………… |  | 139.6 Ah
Internal Resistance
(Fully charged battery @ 25°C /77°F ) …………. | [5 empty] | 4.5mΩ |  | Dimension & Weight
Max. Discharge Current @ 25°C /77°F ………….. | [5 empty] | 1350 A (5S) |  | Dimension (± 2mm) | [7 empty] | Weight (± 2%)
Charge Methods: Constant voltage charge @ 25°C /77°F | [7 empty] | Length |  | Width |  | Height |  | Total Height
Cycle Use ……………………………………… | [5 empty] | 14.7 ~ 14.9V |  | 341 | mm | 171 | mm | 283 | mm | 288 | mm | 41.5 | kg
Max. Current ………………………………….. | [5 empty] | 33 A |  | 13.4252 | inch | 6.7323 | inch | 11.1417 | inch | 11.3386 | inch | 91.4918 | lbs
Standby Use ………………………………….. | [5 empty] | 13.6 - 13.8V
Operating Temperature Range …………………… | [5 empty] | -30 ~ 50°C |  | Typical Applications
Notes: battery voltage must be adjusted according to temperature. | [7 empty] | ○ Telecommunications |  |  | ○ Power Utility |  | ○ Data Center |  | ○ UPS & EPS
Please refer to our recommendation.
Self-Discharge | [7 empty] | Certificates
3% of capacity declined per month @ 25°C (77°F).
Constant Current Discharge (Amperes @ 25°C /77°F)
V/cell | 10min | 15min | 20min | 25min | 30min | 35min | 40min | 45min | 50min | 55min | 1hr | 2hr | 3hr | 4hr | 5hr | 10hr | 20hr
1.6 | 284.1207 | 216.8861 | 187.3638 | 157.8415 | 133.5996 | 132.4322 | 123.4933 | 115.3181 | 107.8255 | 101.3369 | 102.2148 | 55.4155 | 39.4304 | 32.7476 | 26.7747 | 14.3062 | 7.2255
1.65 | 269.7953 | 205.9506 | 178.8798 | 151.809 | 130.0186 | 128.9279 | 120.4299 | 112.6781 | 105.6294 | 99.5846 | 100.8267 | 54.3438 | 38.6752 | 32.061 | 26.1569 | 14.2374 | 7.2255
1.7 | 258.6533 | 197.4453 | 171.817 | 146.1887 | 125.8408 | 124.6589 | 116.4948 | 109.0529 | 102.3402 | 96.6315 | 98.0505 | 52.5095 | 37.7827 | 31.3058 | 25.539 | 14.0998 | 7.2255
1.75 | 246.7155 | 188.3324 | 164.1502 | 139.9679 | 121.0661 | 119.9504 | 112.338 | 105.4238 | 99.2666 | 94.1134 | 95.9684 | 51.0566 | 36.9589 | 30.6193 | 24.9898 | 13.9623 | 7.1579
1.8 | 233.9818 | 178.612 | 156.0784 | 133.5447 | 116.2915 | 115.1335 | 107.9646 | 101.4676 | 95.7568 | 91.05 | 93.1923 | 49.2222 | 36.0664 | 29.8641 | 24.3719 | 13.5983 | 7.0904
Constant Power Discharge (Watts/cell @ 25°C /77°F)
V/cell | 10min | 15min | 20min | 25min | 30min | 35min | 40min | 45min | 50min | 55min | 1hr | 2hr | 3hr | 4hr | 5hr | 10hr | 20hr
1.6 | 493.431 | 376.6649 | 331.4835 | 286.3021 | 249.5694 | 248.0181 | 230.39 | 214.1803 | 199.1119 | 186.386 | 186.3527 | 102.4403 | 74.5474 | 61.8565 | 50.9407 | 28.5435 | 15.0587
1.65 | 475.9221 | 363.2993 | 320.3847 | 277.4701 | 243.0042 | 241.449 | 224.4848 | 208.9041 | 194.504 | 182.4464 | 182.8825 | 100.362 | 73.8608 | 61.17 | 50.2541 | 28.2684 | 15.0587
1.7 | 457.6174 | 349.3263 | 308.4831 | 267.6399 | 235.2454 | 233.7841 | 217.703 | 202.966 | 189.4549 | 178.2863 | 179.4123 | 97.9404 | 72.4878 | 60.1059 | 49.4989 | 27.7182 | 14.8561
1.75 | 437.721 | 334.1382 | 295.5725 | 257.0067 | 226.8897 | 225.4629 | 210.2661 | 196.3698 | 183.7489 | 173.4706 | 175.2481 | 94.8285 | 70.4282 | 58.6298 | 48.6064 | 27.5118 | 14.586
1.8 | 416.2329 | 317.735 | 281.6529 | 245.5707 | 217.9372 | 216.4854 | 202.1743 | 189.1155 | 177.3862 | 167.9994 | 170.3899 | 91.4725 | 68.5745 | 57.1538 | 47.508 | 27.2367 | 14.4509
Subject to revision without notice. Please contact our sales representatives for latest version. | [15 empty] | Page 1 of 2
Web:www.genergybattery.com 丨 Email:sales@genergybattery.com
AGM Standby Use Battery > NM Series
NM12-135
12V135Ah / 10hr rate
Graphs
Subject to revision without notice. Please contact our sales representatives for latest version. | [15 empty] | Page 2 of 2
Web:www.genergybattery.com 丨 Email:sales@genergybattery.com

## Sheet2
316.8065 | 241.837 | 209.8536 | 177.8702 | 152.3868 | 136.6623 | 127.4379 | 118.2135 | 109.1391 | 100.9647 | 94.5402 | 54.4385 | 37.8168 | 31.645 | 25.8733 | 13.8245 | 6.9822
300.8331 | 229.6436 | 199.4585 | 169.2734 | 145.5883 | 130.4875 | 121.8867 | 113.2859 | 104.8351 | 97.2843 | 91.4835 | 52.1925 | 36.3815 | 30.3858 | 24.7901 | 13.4935 | 6.8479
288.4093 | 220.1598 | 191.5831 | 163.0065 | 140.9298 | 126.1669 | 117.904 | 109.6411 | 101.5282 | 94.3153 | 88.8524 | 50.454 | 35.5356 | 29.6701 | 24.2045 | 13.3631 | 6.8479
275.0981 | 209.9985 | 183.0343 | 156.0701 | 135.6059 | 121.4014 | 113.697 | 105.9925 | 98.438 | 91.7836 | 86.8791 | 49.077 | 34.7548 | 29.0194 | 23.684 | 13.2327 | 6.7839
260.8995 | 199.1599 | 174.0339 | 148.9079 | 130.2819 | 116.5263 | 109.2706 | 102.015 | 94.9093 | 88.7037 | 84.2481 | 47.3385 | 33.909 | 28.3037 | 23.0984 | 12.8878 | 6.7199
550.1962 | 419.9971 | 369.6179 | 319.2388 | 274.8597 | 251.0183 | 233.177 | 215.3356 | 198.0943 | 182.953 | 169.3116 | 98.8508 | 71.8699 | 58.6245 | 48.279 | 27.0521 | 14.2719
530.6731 | 405.094 | 357.2424 | 309.3908 | 267.5392 | 244.3698 | 227.2004 | 210.031 | 193.4616 | 178.9922 | 166.0228 | 96.881 | 71.2193 | 57.9738 | 47.6283 | 26.7914 | 14.2719
510.2626 | 389.5134 | 343.9716 | 298.4297 | 258.8878 | 236.6121 | 220.3365 | 204.0609 | 188.3852 | 174.8096 | 162.7339 | 94.586 | 69.918 | 56.9653 | 46.9126 | 26.2699 | 14.0799
488.0773 | 372.5781 | 329.5757 | 286.5733 | 249.5709 | 228.1903 | 212.8097 | 197.4291 | 182.6485 | 169.9679 | 158.7873 | 91.6366 | 67.966 | 55.5664 | 46.0667 | 26.0743 | 13.8239
464.1171 | 354.2879 | 314.0547 | 273.8216 | 239.5885 | 219.1042 | 204.6199 | 190.1357 | 176.2514 | 164.4672 | 154.1829 | 88.4561 | 66.2092 | 54.1674 | 45.0257 | 25.8136 | 13.6959
324.0067 | 247.3333 | 214.623 | 181.9127 | 155.8501 | 139.7683 | 130.3342 | 120.9002 | 111.6195 | 103.2593 | 96.6889 | 55.6757 | 38.6762 | 32.3642 | 26.4613 | 14.1387 | 7.1409
307.6702 | 234.8627 | 203.9916 | 173.1205 | 148.8971 | 133.4531 | 124.6569 | 115.8606 | 107.2177 | 99.4953 | 93.5627 | 53.3787 | 37.2083 | 31.0764 | 25.3536 | 13.8001 | 7.0036
294.9641 | 225.1634 | 195.9373 | 166.7112 | 144.1328 | 129.0344 | 120.5837 | 112.133 | 103.8357 | 96.4589 | 90.8718 | 51.6007 | 36.3433 | 30.3444 | 24.7547 | 13.6668 | 7.0036
281.3503 | 214.7712 | 187.1942 | 159.6171 | 138.6878 | 124.1605 | 116.281 | 108.4014 | 100.6753 | 93.8696 | 88.8537 | 50.1924 | 35.5447 | 29.679 | 24.2223 | 13.5335 | 6.9381
266.829 | 203.6863 | 177.9892 | 152.2922 | 133.2429 | 119.1746 | 111.7541 | 104.3335 | 97.0664 | 90.7197 | 86.1628 | 48.4144 | 34.6796 | 28.947 | 23.6234 | 13.1807 | 6.8727
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562.7007 | 429.5425 | 378.0184 | 326.4942 | 281.1065 | 256.7233 | 238.4765 | 220.2296 | 202.5965 | 187.111 | 173.1596 | 101.0974 | 73.5034 | 59.9568 | 49.3762 | 27.6669 | 14.5962
542.7339 | 414.3007 | 365.3615 | 316.4224 | 273.6197 | 249.9237 | 232.3641 | 214.8044 | 197.8585 | 183.0602 | 169.796 | 99.0829 | 72.8379 | 59.2914 | 48.7108 | 27.4003 | 14.5962
521.8595 | 398.366 | 351.7891 | 305.2122 | 264.7716 | 241.9897 | 225.3442 | 208.6986 | 192.6667 | 178.7825 | 166.4324 | 96.7356 | 71.507 | 58.2599 | 47.9788 | 26.8669 | 14.3998
499.1699 | 381.0458 | 337.066 | 293.0863 | 255.2429 | 233.3764 | 217.6463 | 201.9161 | 186.7996 | 173.8308 | 162.3961 | 93.7193 | 69.5107 | 56.8292 | 47.1137 | 26.6669 | 14.138
474.6652 | 362.3399 | 321.1923 | 280.0448 | 245.0337 | 224.0838 | 209.2704 | 194.457 | 180.2571 | 168.2051 | 157.6871 | 90.4664 | 67.714 | 55.3985 | 46.049 | 26.4003 | 14.0071
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331.3705 | 252.9545 | 219.5008 | 186.0471 | 159.3921 | 142.9449 | 133.2964 | 123.6479 | 114.1563 | 105.6061 | 98.8863 | 56.9411 | 39.5552 | 33.0998 | 27.0627 | 14.46 | 7.3032